## Slide 1
AGC 150
Basic knowledge

## Slide 2
Synchronizing Controllers
GPC-3
Base mounted
Non-Power Management
AGC 200
Front mounted
Standard Power Management
AGC-4
Base mounted
Custom Power Management
AGC 150
Front mounted
Simple Power Management

## Slide 3
Documentation
www.deif.com contains all manuals for the controllers

## Slide 4
Documentation

## Slide 5
AGC 150
AUTO
SEMI AUTO
Shortcut Menu

## Slide 6
AGC 150
GOV / AVR
-10… 10VDC
PWM
USB
Ethernet TCP/IP
Additional I/O
ECU
DEIF PMS
RS485 (1)
RS485 (2)

## Slide 7
Typical wiring

## Slide 8
Setup Current Transformer
Basic Settings
Configurable CT

## Slide 9
Nominal settings
Basic Settings
Configurable CT

## Slide 10
Start Sequence
1. Before starting, start prepare ON (Relay 9). Can be used to activate pre-heating element.
If not required, timer can be changed to 0s to reduce starting time.
2. Shortly after, Starter/crank (relay 6) and Run coil (relay 5), both ON.
Once running feedback detected, Starter/crank is deactivated.
3. Run coil activates continuously all the time, for the duration of engine running.
Glow plug
starting
running

## Slide 11
Generator Protection
Checkmark [ √ ] = enable
And many more protections…

## Slide 12
Generator Protection
Fail class:
Trip + stop = GB trip, engine stop after cooling down
Safety stop = Extra genset start up & replace faulty genset
Trip MB/GB = In application “Single DG with mains”, will trip MB instead

## Slide 13
I/O
DIGITAL INPUT
DIGITAL OUTPUT
ANALOG INPUT

## Slide 14
Digital Input
12 digital inputs, activated by negative (-) VDC signal
Each can be configured as:
1. Alarms  setup by Display or USW
2. Function  setup by USW only

## Slide 15
Digital Input
1. Digital input as alarm
Parameter > I/O settings > Inputs > Digital inputs
[ √ ] to enable
Set delay
Action

## Slide 16
Digital Input
2. Digital input as Function
Click icon I/O settings
Configuration input/output settings

## Slide 17
Digital Input
Default assignment
Terminal no. | Function | Remarks
39 | Auto start/stop | For remote start signal
40 | Not used | 
41 | Not used | 
42 | Not used | 
43 | Not used | 
44 | Not used | 
45 | Not used | 
46 | Not used | 
47 | Status MB ON | For application with Mains
48 | Status MB OFF | For application with Mains
49 | Status GB ON | 
50 | Status GB OFF | 

## Slide 18
Digital Output
12 digital outputs (DC outputs)
Require common positive (+) VDC
Configuration by USW
(+) VDC

## Slide 19
Digital Output
Setup digital output
Click icon I/O settings
Configuration input/output settings

## Slide 20
Digital output
Default assignment:
Terminal no. | Function | Remarks
4 | Common (+) for DO 5-6 | Also serves as Emergency stop
5 | Run coil | 
6 | Starter (crank) | 
---------------- | --------------------------------- | ---------------------------------------------
8 | Common (+) for DO 9-18 | 
9 | Start prepare | 
10 | Stop coil | 
11 | Status OK | 
12 | Horn | 
13 | Not used | 
14 | Not used | 
15 | MB ON | For application with Mains
16 | MB OFF | For application with Mains
17 | GB ON | 
18 | GB OFF | 

## Slide 21
Analog Input
4 multi inputs
Selectable for:
- 4-20 mA - RMI Oil Pressure
- 0-10 VDC - RMI Water Temperature
- PT100 - RMI Fuel Level
- Binary input
Setup by USW

## Slide 22
Analog Input
Configuring multi inputs

## Slide 23
Input & Output Text
To change text, use Translations

## Slide 24
Input & Output Status
Any digital input/output can be monitored trough USW and display

## Slide 25
Analog Regulation
SPEED REGULATION - ANALOG
VOLTAGE REGULATION - ANALOG

## Slide 26
Speed Regulation - Analog
Setup terminal analog output
Parameter > Engine > Gov > General configuration
Set as analog
Set transducer 52
More setting

## Slide 27
Speed Regulation - Analog
2. Setting analog output range (VDC)
Parameter > Engine > Gov > General configuration > AOUT 52 limits
0 %
100 %
50 %
GOV
-10V
10V

## Slide 28
Speed Regulation - Analog
3. Setting offset / center
Parameter > Engine > Gov > Offset for control signal
0 %
100 %
50 %
GOV
-10V
10V
0V

## Slide 29
Speed Regulation – Analog Gain
1. PID Island
Parameter > Engine > Gov > Speed PID
> Island (analog/EIC)
Running

## Slide 30
Speed Regulation – Analog Gain
2. PID Load sharing
Parameter > Engine > Gov > Speed PID
> Load share (analog/EIC)
close
other gensets

## Slide 31
Speed Regulation – Analog Gain
3. PID Mains parallel
Parameter > Engine > Gov > Speed PID
> Mains parallel (analog/EIC)
close

## Slide 32
Voltage Regulation - Analog
Setup terminal analog output
Parameter > Generator > AVR > General configuration
More setting

## Slide 33
Voltage Regulation - Analog
2. Setting analog output range & center
Parameter > Generator > AVR > General configuration > AOUT 55 limits
Parameter > Generator > AVR > Offset for control signal
0 %
100 %
50 %
AVR
-10V
10V
0V

## Slide 34
Voltage Regulation – Analog Gain
Same principle with speed PID
Parameter > Generator > AVR > Voltage PID >
Island (analog/EIC)
Load share (analog/EIC)
Mains parallel (analog/EIC)

## Slide 35
Analog Regulation Status
Check Device
> Governor reg.
> AVR reg.

## Slide 36
Relay regulation
SPEED REGULATION - RELAY
VOLTAGE REGULATION - RELAY

## Slide 37
Speed Regulation - Relay
1. Change Gov setting to relay
Parameter > Engine > Gov > General configuration
Select “Relay”
ignore this part..

## Slide 38
Speed Regulation - Relay
2. Setup pulse signal and choosing relay terminals
Parameter > Engine > Gov > Relay configuration > Output and period
Select any unused DO
Increase
Decrease

## Slide 39
Speed Regulation - Relay
3. Setup speed Gain
Parameter > Engine > Gov > Speed PID >
Island (relay)
Load share (relay)
Mains Parallel (relay)

## Slide 40
Speed Regulation - Relay
Regulation Deadband
Signal length depends on the Kp value and size of the deviation.
Gov relay inactive inside deadband window
Regulation signal
When commissioning, set deadband to minimum to check genset response
After completed, set deadband back to prolong relay lifetime

## Slide 41
Voltage Regulation - Relay
1. Change AVR setting to relay
Parameter > Generator > AVR > General configuration
Select “Relay”
ignore this setting

## Slide 42
Voltage Regulation - Relay
2. Setup pulse signal and choosing relay terminals
Parameter > Generator > AVR > Relay configuration > Output and period
Select any unused DO
Relay Increase
Relay Decrease

## Slide 43
Voltage Regulation - Relay
3. Setup voltage Gain
Parameter > Generator > AVR > Voltage PID >
Island (relay)
Load share (relay)
Mains Parallel (relay)
When commissioning, set deadband to minimum to check genset response
After completed, set deadband back to prolong relay lifetime

## Slide 44
Relay Regulation Status
Check Device
> Governor reg.
> AVR reg.

## Slide 45
Synchronisation

## Slide 46
Synchronisation
AGC always perform synchronism check before closing breakers
All modes: Auto, Semi Auto, and Manual
Genset should run slightly faster than bus
to avoid reverse power (f gen > f bus)
50.0Hz
50.1Hz
49.9Hz
√
Allowed maximum slip frequency: 0.3Hz

## Slide 47
Synchronisation
Change slip frequency & voltage
Synchronisation > Dynamic synchronisation
Slip Frequency
Slip Voltage
Here, to sync with 50.0Hz 400V busbar, genset need to run:
- Freq between 50.0 – 50.3Hz
- Voltage between 380 – 420V
Normally no need changing these settings

## Slide 48
Application
SINGLE GENSET
MULTIPLE GENSETS

## Slide 49
Adapting Mimic
Standalone AMF
Genset
BTB
MAINS
MAINS+TB
Standalone Parallel without MB
Standalone Island

## Slide 50
Typical Applications for AGC 150
Single Genset
Single Genset with Mains
Multiple Genset’s with Mains
Genset 1
Genset 2
Genset 32 (SW packagers dependent)
Single Genset
Single Genset w. Mains
Genset 3
Mains

## Slide 51
Application
SINGLE GENSET

## Slide 52
Single Genset
Application configuration
New plant configuration
“Single DG”
Mains
Single Genset
with Mains

## Slide 53
Single Genset
Alternative setup:*
Access from AGC 150 display:
Settings > Basic settings > Application type > Standalone or PM >
> Application select > Active Application
change active application from [1] to [2]
*Only works if application 2 in default factory setting
Application 2
Application 1

## Slide 54
Single Genset
Select Genset Mode
Parameter > Basic settings > Application type > Genset type > Genset/plant mode
Example: AMF

## Slide 55
Single Genset
Enable Back Synchronising
Parameter > Synchronisation > Mains parallel settings

## Slide 56
Single Genset
AMF delay settings
Parameter > Mains > AMF function > AMF timer
Modeshift ON: Other modes retain AMF function when Mains fail
Mains failure delay
Mains Ok delay

## Slide 57
Single Genset
Mains failure voltage setpoint
Parameter > Mains > Voltage and frequency limits > Voltage limits

## Slide 58
Single Genset
Done setup single genset?
Check Application Supervision

## Slide 59
Single Genset
Or Device
For detailed monitoring

## Slide 60
Application
MULTIPLE GENSETS

## Slide 61
Multiple Gensets
 Application configuration
 New plant configuration
Genset 1
Genset 2
“Standard”
Create drawing
of 2 gensets
2 Gensets

## Slide 62
Multiple Gensets
Select Genset Mode
Parameter > Basic settings > Application type > Genset type > Genset/plant mode
Genset 1
Genset 2
select power management
Power management
Power management
Load sharing

## Slide 63
Multiple Gensets
Setup ID Number
Parameter > Communication > Power management ID
Genset 1
Genset 2
ID: 1
ID: 2
add ID on every genset

## Slide 64
Multiple Gensets
CANbus wiring
Genset 1
Genset 2
put resistor 120 Ω
on both ends
CAN PMS

## Slide 65
Multiple Gensets
Check Application Supervision
Incorrect communication will be shown
Genset 1
Genset 2

## Slide 66
Power Management
LOAD DEPENDENT START/STOP
MULTI START
Genset 1
Genset 2

## Slide 67
Load dependent start/stop
Configure Start/stop based on load Percentage
Parameter > Power management > Load dependent start/stop configuration
Genset 1
Genset 2
Set as Percentage

## Slide 68
Load dependent start/stop
Start percentage setpoint
Parameter > Power management > Load dependent start 1
Genset 1
Genset 2
Start delay

## Slide 69
Load dependent start/stop
Stop percentage setpoint
Parameter > Power management > Load dependent stop 1
Genset 1
Genset 2
Stopping delay
% capacity after 1 genset removed

## Slide 70
Multi start
Setup of how many gensets start together
Parameter > Power management > Multi start set
Genset 1
Genset 2
Autostart/stop input
Select Start 2 DG
Start
Start